## Elevator and Dumbwaiter
PROJECT NAME: Total Club House
Elevator and Dumbwaiter
[5 empty] | RATE | RATE | TOTAL
ITEM | DESCRIPTION | QTY | UNIT | MAKE & CAT REF | DELIVERED | INSTALLED | AMOUNT
[5 empty] | =N= | =N= | =N=
A | Elevator: Machine roomless (MRL) | 1 | Nr
i | Main supply system; AC 415Volts, 3 Phase, 50Hz with statutory variation operating
speed of 1.0m/s
ii | Maximum capacity (no. of passengers)/weight in kg: 12/900kg (Minimum)
iii | Size of lift well
1600mmW and 1950mmD with a pit depth of 1400mm. Vendor to confirm if the size will
be suitable for a 900Kg Car (minimum)
iv | Overhead is 3850mm and 3.6m between floors. Vendor to confirm with structural drawings
before final order from OEM
v | Number of landing: 3
vi | Interior enclosure to have Stainless Steel (SS), with Grade 304, with full glazing at the
opposite end of the entrance door with hand rails. Architect to determine final finish, not
limited to floor, ceiling, type of control button etc.
vii | Center opening type car (900mm width) and landing doors, electromagnetic brake system,
operating panel with luminous button, overload warning indicator, battery operated alarm bell,
emergency light, intercom suitable for hook up to facility's EPABX, photocell sensing door
protection for full height (min. of 2000mm height) and mechanical safety by pressure sensor,
reverse phase relay on controller, fire man's switch at ground floor.
viii | Landing operating devices:
The following are to be provided as per manaufacturers specification:
a | Car Call button, Full Collective
b | Fire man's switch
c | Rescue device with an emergency landing kit.
d | UPS provison | 1 | Nr
ix | Landing indicating devices:
The following are to be provided as per manaufacturers specification:
a | Landing call registering indicator, Car
b | Up direction travel, Landing in all floor
c | Down direction travel, Landing in all floor
d | Floor positioning indicator, Landing in all floor
All cable to be pre-wired with respective sockets.
B | Dumbwaiter | 1 | Nr
i | Nominal speed: 0.3m/s
ii | Stops: 3
iii | Dimension of shaft: 1800mmD x 1800mmW.
iv | Overhead: Based on the architectural provision
v | Driving system: Winding drum
vi | Rail: Steel Type
vii | Call button: Stainless steel, push button, indicating of door close/open with an arrival buzz.
viii | Car specification:
Door width between 800 to 1000mm
Pit depth of 750mm
All cable to be pre-wired with respective sockets.